The Pennsylvania State University

Hot Work Permit Program

Contents:

(	Purpose

(	Application

(	Reference

(	Definitions

(	Procedures

(	Responsibilities

(	Appendix A. Hot Work Permit

PURPOSE:

To provide written procedures to prevent the outbreak of fire, fire alarm activations, and smoke and odor migration in buildings resulting from any temporary operation involving the use of open flames or which produces heat and / or sparks.

This includes, but is not limited to: brazing, cutting, grinding, torch soldering, thawing pipes, torch applied roofing and welding.

APPLICATION:

This procedure applies to work performed by any Penn State University employee, student and contractors performing work in existing buildings, new construction in existing buildings or new construction attached to existing buildings.

This procedure does not apply to new construction where there is no attachment to existing buildings or to areas that are specifically designed and equipped for such operations, i.e. maintenance shop areas and designated welding areas or to Hershey Medical Center Facilities.

REFERENCES:

FM Global - Factory Mutual Insurance Company “Hot Work Guidelines”

National Fire Protection Association Standard 51B “Standard for Fire Prevention During Welding, Cutting and Other Hot Work”.

International Fire Code 2009 Edition Chapter 26 “Welding and Other Hot Work”

OSHA Regulations 29 CFR 1926.352 “Welding and Cutting”

DEFINITIONS:

Hot Work:

Any operation producing flame, sparks or heat including cutting, welding, brazing, grinding, sawing, torch soldering, thawing frozen pipes, applying roof covering etc.

Permit:

A special permit, which authorizes “Hot Work” activities at a specific location and time. The permit which is available from the Environmental Health and Safety Web Page (www.ehs.psu.edu) will be properly filled out, displayed on site and returned to the employees supervisor when the hot work is complete.

Permits contain a checklist to be completed prior to commencing hot work activities and also at the conclusion of the hot work.

Fire Watch:

A trained individual stationed in the hot work area who monitors the work area for the beginnings of potential, unwanted fires both during and after hot work. Individuals must be trained and familiar with the operation of portable fire extinguishers and methods to activate building fire alarm systems.

PROCEDURES:

- Hot work should not be performed if the work can be avoided or performed in a safer manner. When practical, objects to be welded, cut or heated should be moved to a designated safe location, i.e. maintenance shops.

2. 	If hot work must be performed, a Hot Work Permit must be completed.

- All precautions on the Hot Work Permit must be met prior to any work commencing. The supervisor or the employee performing the hot work will complete the permit.

- The Hot Work Permit is only good for the date specified on the permit.

- A Hot Work Permit must be displayed at the work site during all hot work activities.

- All building occupants must be suitably protected against hazards generated by the work. i.e. heat, sparks, fumes, welding rays, etc.

- Before hot work begins:

  - An appropriate fire extinguisher must be available and operable.

  - Flammable and ignitable materials and debris must be moved at least 35 feet from the hot work area or covered and protected from the hot work by fire resistant material.

  - Explosives, compressed gas cylinders or stored fuel must be moved at least 50 feet from the hot work area or covered and protected from the hot work by fire resistant material.

  - Smoke and fire detectors in the immediate area of the hot work must be temporarily disabled until the hot work is completed.

  - Adequate ventilation is being used (especially when cutting or welding materials with painted or metal coated surfaces).

  - Building occupants have been protected or isolated from the hot work area.

  - Cracks or holes in floors, walls, and ceilings (including ductwork) are properly covered or plugged.

  - Hot work equipment is operable and in good repair.

  - Drums, barrels and tanks have been cleaned and purged of flammables and toxics, all tank feeds are closed, and the tank vented.

  - A Fire watch is implemented if conditions warrant. If no fire hazards or combustible exposures are present a fire watch is not required.

  - Workers and Fire Watch personnel are trained in the use of fire extinguishing equipment and how to sound a fire alarm.

- When hot work is complete:

  - The work area and any potentially affected surrounding areas are inspected for fire, fire damage or the potential for fire for a minimum of 30 minutes following completion of the hot work.

  - Smoke / fire alarms that were disabled because of hot work are reactivated.

  - Hot work permit is closed out

  - Completed permit is returned to workers supervisor who then submits the completed permit to the Environmental Health and Safety Office.

RESPONSIBILITIES:

# Management

It is the responsibility of management to insure that this policy is implemented in those areas under their jurisdiction where applicable.

# Environmental Health and Safety

- Develop written Hot Work Program and revise the program as necessary

- Provide Hot Work procedure training program for supervisors and employees

- Periodically audit operations, documentation and training

# Safety Officers

- Be thoroughly familiar with the Hot Work procedures

- Implement the Hot Work Program in Work Units

# Supervisors including Faculty and Instructors

- Be thoroughly familiar with the Hot Work procedures

- Identify employees who may perform hot work as defined in this procedure

- Provide Hot Work training to employees who perform Hot Work operations

- Maintain records of employee training

- Provide Hot Work Permits

- Collect and complete Hot Work Permits and send to the University Fire Protection Engineer at Environmental Health and Safety.

- Ensure compliance with procedures by employees

- Complete EHS training program

# Employees

- Be thoroughly familiar with Hot Work procedures

- Follow all Hot Work procedures

- Complete Hot Work Permits

- Complete EHS training program

# Students

1. Be thoroughly familiar with Hot Work procedures

# Appendix A

[Copy of Hot Work Permit]

June 2004

Update 8/14 – IFC Standard Edition Date